Observation report Integra 1630 configurator V1.0.0

The configurator will not allow pulse rates of greater than 1 per second to be set.  If a pulse rate between 1 pulse per second and two pulses per second is required, set it via the front panel display.

If using a baud rate of 38400 with the Integra 1630 configurator, do not run the Integra 1530/1560 configurator on the same machine before rebooting that machine.

As detailed in the help file, if changing system type, ensure the Integra is power cycled after changing system type and before attempting to set other parameters on that Integra.

October 2006.